## 180A_PO001
RO Plant 1st Line Maintenance Checklist
Version 2.0 21 - Nov - 2025
Daily Maintenance Action Checklist
Inspection Date | Shift | Operator
2026-01-01 | Day | salavei |  |  | 1
Equipment/Area: 1st Pass High Pressure Pumps |  |  |  |  | 1
1
Tag Number | Functional Location | Equipment
180B_PO001 |  | 160000047 |  |  | 1
Step No. | Action | Checklist Item | Value | Result
1 | Visual Inspection | No water leakage from mechanical seal |  | Pass | 1
|  | No leakage from suction/discharge flanges or couplings |  | Pass | 1
|  | Pump casing, base frame & fasteners intact (no cracks, corrosion) |  | Pass | 1
|  | Motor–pump alignment visually normal (no shift of coupling guard) |  | Pass | 1
|  | No salt deposits around mechanical seal or motor feet |  | Pass | 1
|  | No rust streaks indicating early gasket/packing failure |  | Pass | 1
|  | Area around pump clean & accessible |  | Pass | 1
Step No. | Action | Checklist Item
2 | Noise Inspection | No cavitation noise (crackling / popping) |  | Pass | 1
|  | No grinding, rattling, or metallic contact |  | Pass | 1
Noise Level (dB):
Step No. | Action | Checklist Item
3 | Thermal Check | Pump casing temperature normal
|  | Pump Casing temperature (°C): | 33 | Pass | 1
Acceptable Range: Ambient + 20°C tot max 80°C
|  | Bearing housing temperature normal |  | Pass | 1
|  | Pump Bearing NDE temperature (°C): | 86 | Pass | 1
(Max: 90°C)
|  | Pump Bearing DE temperature (°C): | 87 | Pass | 1
(Max: 95°C)
|  | No hotspots detected on pump casing |  | Pass | 1
Step No. | Action | Checklist Item
4 | Parameter Check | Suction Pressure (bar):
(Min. 1 (bar) Max. 5 (bar)
Discharge Pressure (bar):
(Min. 50 (bar) Max. 56 (bar)
Flow Rate (m³/h):
(Min. 275 (m³/h) Max. 710 (m³/h))
Pump speed (RPM)
Min. 2950 (RPM) Max. 3000 (RPM)
Pump Capacity (kW)
Min. 480 (kW) Max. 590 (kW)
Stable pump operation (no oscillation or surge)
No SCADA alarms (seal leakage, overload, low suction, vibration)
Step No. | Action | Checklist Item
5 | Mechanical/Functional | No abnormal vibration on pump | 4 |  | 1
Vibration Level: (Vrms ≤ 4.5 mm/s) according to ISO 20816-1 is acceptable in coupled-mode operation.
|  | No visible wear/damage on coupling guard |  | Pass | 1
|  | Flow stable, no sudden drops or spikes |  | Pass | 1
|  | No backpressure shock or reverse flow tendency |  | Pass | 1
Step No. | Action | Checklist Item
6 | Electrical Check | No loose conduit fittings / cable damage |  | Pass | 1
|  | Motor cooling fan unobstructed |  | Pass | 1
|  | Local transmitters functioning |  | Pass | 1
|  | No overload or thermal alarms |  | Pass | 1
Step No. | Action | Checklist Item
7 | Record Observations | Document any abnormal findings, trends or early warnings |  | Done | 1
| Log Hours | Total Operating Hours. Take note from motor controller or logbook | 1 |  | 1
| Create Notification | Indicate whether a Notification should be creaed |  | Yes | 1
Enter your notes below if any issues or observations need to be recorded.
no issuers found |  |  |  |  | 29
Submit

## Sheet2 (hidden)
Tag ID | Functional Location | Equipment
180A_PO001 |  | 160000044
180B_PO001 |  | 160000047
180C_PO001 |  | 160000050
180D_PO001 |  | 160000053